BAT-12V17AH             12V17AH/20HR

Small-Size

Standard Terminal Dimensions

Battery Construction

Small Size VRLA batteries enjoy excellent discharge performance, and they have low self-discharge and large-current resistance capacity. Small-size batteries are capable for a wide range of applications. Their designed service life is 3-5 years, and we provide 12-month quality warranty for them. Our batteries can meet with many demanding technical and quality requirements form our customers.

Application

- Emergency lighting

- Security and burglar alarm systems

- Electric toys and power tools

- Telephone and telecommunication equipment

- Computer UPS

- Medical equipments and instruments

General Features

- Sealed and maintenance free operation

- Not restricted from air transport-complies with IATA/ICAO Special Provision A67.

- UL-recognized components

- Safety valve installation for explosion proof

- Excellent deep discharge recovery performance

- Low self-discharge ratio

- Long service life, float or cycle-use applications

| Component | Positive plate | Negative plate | Container | Cover | Safety valve | Terminal | Separator | Electrolyte |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Material | Lead dioxide | Lead | ABS | ABS | Rubber | Copper | AGM glass | Sulfuric acid |

BAT-12V17AH             12V17AH/20HR

General Specifications

| Battery Model | BAT-12V17AH(12V17AH/20 HR) |
| --- | --- |
| Designed Service Life | 5 years |
| Capacity (25℃) | 20HR (0.85A) | 10HR (1.53A) | 5HR (2.90A) | 1HR (11.1A) |
|  | 17.0AH | 15.3AH | 14.5AH | 11.1AH |
| Dimension: mm (inch) | Length | Width | Height | Total Height |
|  | 181 (7.13) | 77(3.03) | 167(6.57) | 167(6.57) |
| Approx. Weight | 5.15Kg (11.36 lbs) |
| Internal Resistance | Fully charged at 25℃: 0.03 Ohm |
| Self-discharge | 3% of capacity declined per month at 25℃ |
| Capacity Affected by Temp. (20HR) | 40℃ | 25℃ | 0℃ | -15℃ |
|  | 105% | 100% | 85% | 65% |
| Charge Voltage (25℃) | Cycle use | Stand-by use |
|  | 14.40-15.00V(-30mV/℃) Max. Current: 5.1A | 13.50-13.80V (-20mV/℃) |

Performance Curves and Charts

| Discharge Characteristic (25℃) | Charge Characteristic (25℃) |
| --- | --- |
| Effect of temperature on capacity | Number of cycles Vs. Depth of Discharge |

BAT-12V17AH         12V17AH/20HR

Constant Current Discharge Data

| Constant Current Discharge Data Sheet (Amperes at 25℃) |
| --- |
| End Voltage/cell | Minute (s) | Hour (s) |
|  | 5 | 10 | 15 | 30 | 1 | 3 | 5 | 10 | 20 |
| 1.80 | 65.9 | 44.7 | 34.9 | 20.4 | 12.2 | 4.88 | 3.24 | 1.65 | 0.84 |
| 1.75 | 67.6 | 46.0 | 35.8 | 20.7 | 12.4 | 4.96 | 3.31 | 1.69 | 0.85 |
| 1.70 | 69.3 | 47.2 | 36.7 | 21.0 | 12.6 | 5.04 | 3.37 | 1.73 | 0.90 |
| 1.65 | 71.1 | 48.4 | 37.5 | 21.4 | 12.8 | 5.12 | 3.44 | 1.76 | 0.91 |
| 1.60 | 72.8 | 49.7 | 38.4 | 21.7 | 13.0 | 5.20 | 3.50 | 1.79 | 0.92 |

Constant Power Discharge Data

| Constant Power Discharge Data Sheet (Watts at 25℃) |
| --- |
| End Voltage/cell | Minute (s) | Hour (s) |
|  | 5 | 10 | 15 | 30 | 45 | 1 | 2 | 3 | 5 |
| 1.80 | 128 | 94.9 | 76.0 | 42.0 | 32.6 | 25.5 | 14.2 | 9.94 | 6.78 |
| 1.75 | 133 | 96.3 | 77.3 | 42.7 | 33.0 | 25.8 | 14.4 | 10.0 | 6.79 |
| 1.70 | 138 | 98.2 | 78.7 | 43.3 | 33.40 | 26.0 | 14.5 | 10.1 | 6.88 |
| 1.65 | 143 | 100 | 80.1 | 43.9 | 33.8 | 26.3 | 14.7 | 10.2 | 6.96 |
| 1.60 | 147 | 102 | 81.5 | 44.6 | 34.2 | 26.6 | 214.9 | 10.3 | 7.05 |

End Voltage

| Discharge Rate | Discharge Current | End Voltage（V/cell） |
| --- | --- | --- |
| 20h | 0.05C20 A (I20) | 1.75 |
| 10h | 0.09C20 A (I10) | 1.75 |
| 3h | 0.25C20 A (I3) | 1.75 |
| 1h | 0.60C20 A (I1) | 1.60 |

Storage Time VS Charge Time

| Storage Time | Top up Charging Recommendation |
| --- | --- |
| Less than 6 months from production or previous top up charge | Maximum of 16 hours at a constant voltage of 2.40VPC |
| Less than 12 months from production or previous top up charge | Maximum of 20 hours at a constant voltage of 2.40VPC |
| Less than 6 months from production or previous top up charge | Maximum of 8 hours at a constant current of 0.1 C A |
| Less than 12 months from production or previous top up charge | Maximum of 10 hours at a constant current of 0.1 C A |