BAT-12V5AH           12V5AH/20HR

Standard Terminal Dimensions

Battery Construction

Small-size

Small Size VRLA batteries enjoy excellent discharge performance, and they have low self-discharge and large-current resistance capacity. Small size batteries are capable for a wide range of applications. Their designed service life is 3-5 years, and we provide 12-month quality warranty for them. Our batteries can meet with many demanding technical and quality requirements form our customers.

Application

- Emergency lighting

- Security and burglar alarm systems

- Electric toys and power tools

- Telephone and telecommunication equipment

- Computer UPS

- Medical equipments and instruments

General Features

- Sealed and maintenance free operation

- Not restricted from air transport-complies with IATA/ICAO Special Provision A67.

- UL-recognized components

- Safety valve installation for explosion proof

- Excellent deep discharge recovery performance

- Low self-discharge ratio

- Long service life, float or cycle-use applications

| Component | Positive plate | Negative plate | Container | Cover | Safety valve | Terminal | Separator | Electrolyte |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Material | Lead dioxide | Lead | ABS | ABS | Rubber | Copper | AGM glass | Sulfuric acid |

BAT-12V5AH         12V5AH/20HR

General Specifications

| Battery Model | BAT-12V5AH(12V5AH/20 HR) |
| --- | --- |
| Designed Service Life | 5 years |
| Capacity (25℃) | 20HR (0.60A) | 10HR (1.08A) | 5HR (2.04A) | 1HR (7.8A) |
|  | 5.0AH | 4.6AH | 4.25AH | 3.0AH |
| Dimension: mm | Length | Width | Height | Total Height |
|  | 90 | 70 | 101 | 106 |
| Approx. Weight | 1.60Kg |
| Internal Resistance | Fully charged at 25℃: 0.03 Ohm |
| Self-discharge | 3% of capacity declined per month at 25℃ |
| Capacity Affected by Temp. (20HR) | 40℃ | 25℃ | 0℃ | -15℃ |
|  | 105% | 100% | 85% | 65% |
| Charge Voltage (25℃) | Cycle use | Stand-by use |
|  | 14.40-15.00V(-30mV/℃) Max. Current: 3.6A | 13.50-13.80V (-20mV/℃) |

Performance Curves and Charts

| Discharge Characteristic (25℃) | Charge Characteristic (25℃) |
| --- | --- |
| Effect of temperature on capacity | Number of cycles Vs. Depth of Discharge |

BAT-12V5AH            12V5AH/20HR

End Voltage

| Discharge Rate | Discharge Current | End Voltage（V/cell） |
| --- | --- | --- |
| 20h | 0.05C20 A (I20) | 1.75 |
| 10h | 0.09C20 A (I10) | 1.75 |
| 3h | 0.25C20 A (I3) | 1.75 |
| 1h | 0.60C20 A (I1) | 1.60 |

Storage Time VS Charge Time

| Storage Time | Top up Charging Recommendation |
| --- | --- |
| Less than 6 months from production or previous top up charge | Maximum of 16 hours at a constant voltage of 2.40VPC |
| Less than 12 months from production or previous top up charge | Maximum of 20 hours at a constant voltage of 2.40VPC |
| Less than 6 months from production or previous top up charge | Maximum of 8 hours at a constant current of 0.1 C A |
| Less than 12 months from production or previous top up charge | Maximum of 10 hours at a constant current of 0.1 C A |