BAT-6V4.5AH        6V4.5AH/20HR

Standard Terminal Dimensions

Battery Construction

Small Size

Small Size VRLA batteries enjoy excellent discharge performance, and they have low self-discharge and large-current resistance capacity. Small size batteries are capable for a wide range of applications. Their designed service life is 3-5 years, and we provide 12-month quality warranty for them. Our batteries can meet with many demanding technical and quality requirements form our customers.

Application

- Emergency lighting

- Security and burglar alarm systems

- Electric toys and power tools

- Telephone and telecommunication equipment

- Computer UPS

- Medical equipments and instruments

General Features

- Sealed and maintenance free operation

- Not restricted from air transport-complies with IATA/ICAO Special Provision A67.

- UL-recognized components

- Safety valve installation for explosion proof

- Excellent deep discharge recovery performance

- Low self-discharge ratio

- Long service life, float or cycle-use applications.

| Component | Positive plate | Negative plate | Container | Cover | Safety valve | Terminal | Separator | Electrolyte |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Material | Lead dioxide | Lead | ABS | ABS | Rubber | Copper | AGM glass | Sulfuric acid |

BAT-6V4.5AH     6V4.5AH/20HR

General Specifications

| Battery Model | BAT-6V4.5AH (6V4.5AH/20HR) |
| --- | --- |
| Designed Service Life | 5 years |
| Capacity (25℃) | 20HR (0.20A) | 10HR (0.36A) | 5HR (0.68A) | 1HR (2.60A) |
|  | 4.7AH | 4.2AH | 3.8AH | 3.0AH |
| Dimension: mm (inch) | Length | Width | Height | Total Height |
|  | 70 (2.76) | 47 (1.85) | 101 (3.98) | 106 (4.17) |
| Approx. Weight | 0.78 Kg (1.72 lbs) |
| Internal Resistance | Fully charged at 25℃: 0.035 Ohm |
| Self-discharge | 3% of capacity declined per month at 25℃ |
| Capacity Affected by Temp. (20HR) | 40℃ | 25℃ | 0℃ | -15℃ |
|  | 105% | 100% | 85% | 65% |
| Charge Voltage (25℃) | Cycle use | Stand-by use |
|  | 7.20-7.50V(-30mV/℃), Max. Current: 1.20A | 6.75-6.90V (-20mV/℃) |

Performance Curves and Charts

| Discharge Characteristic (25℃) | Charge Characteristic (25℃) |
| --- | --- |
| Effect of temperature on capacity | Number of cycles Vs. Depth of Discharge |

BAT-6V4.5AH      6V4.5AH/20HR

Constant Current Discharge Data

| Constant Current Discharge Data Sheet (Amperes at 25℃) |
| --- |
| End Voltage/cell | Minute (s) | Hour (s) |
|  | 5 | 10 | 15 | 30 | 1 | 3 | 5 | 10 | 20 |
| 1.80 | 11.90 | 8.35 | 7.07 | 4.14 | 2.56 | 1.08 | 0.67 | 0.37 | 0.20 |
| 1.75 | 12.90 | 9.05 | 7.19 | 4.25 | 2.63 | 1.11 | 0.67 | 0.38 | 0.20 |
| 1.70 | 13.30 | 9.22 | 7.33 | 4.32 | 2.67 | 1.13 | 0.69 | 0.39 | 0.20 |
| 1.65 | 13.70 | 9.40 | 7.42 | 4.37 | 2.69 | 1.16 | 0.71 | 0.40 | 0.21 |
| 1.60 | 14.10 | 9.48 | 7.50 | 4.42 | 2.71 | 1.18 | 0.72 | 0.40 | 0.21 |

Constant Power Discharge Data

| Constant Power Discharge Data Sheet (Watts at 25℃) |
| --- |
| End Voltage/cell | Minute (s) | Hour (s) |
|  | 5 | 10 | 15 | 30 | 45 | 1 | 2 | 3 | 5 |
| 1.80 | 22.70 | 15.90 | 13.30 | 7.84 | 5.87 | 4.89 | 2.76 | 2.04 | 1.40 |
| 1.75 | 24.20 | 17.20 | 13.50 | 8.01 | 6.01 | 5.00 | 2.82 | 2.09 | 1.42 |
| 1.70 | 25.10 | 17.40 | 13.60 | 8.16 | 6.08 | 5.06 | 2.85 | 2.11 | 1.45 |
| 1.65 | 25.80 | 17.70 | 13.70 | 8.14 | 6.09 | 5.06 | 2.88 | 2.15 | 1.48 |
| 1.60 | 26.30 | 17.70 | 13.80 | 8.19 | 6.11 | 5.07 | 2.90 | 2.18 | 1.49 |

End Voltage

| Discharge Rate | Discharge Current | End Voltage（V/cell） |
| --- | --- | --- |
| 20h | 0.05C20 A (I20) | 1.75 |
| 10h | 0.09C20 A (I10) | 1.75 |
| 3h | 0.25C20 A (I3) | 1.75 |
| 1h | 0.60C20 A (I1) | 1.60 |

Storage Time VS Charge Time

| Storage Time | Top up Charging Recommendation |
| --- | --- |
| Less than 6 months from production or previous top up charge | Maximum of 16 hours at a constant voltage of 2.40VPC |
| Less than 12 months from production or previous top up charge | Maximum of 20 hours at a constant voltage of 2.40VPC |
| Less than 6 months from production or previous top up charge | Maximum of 8 hours at a constant current of 0.1 C A |
| Less than 12 months from production or previous top up charge | Maximum of 10 hours at a constant current of 0.1 C A |