BAT-12V12AH           12V12AH/20HR

Standard Terminal Dimensions

Battery Construction

Small-size

Small Size VRLA batteries enjoy excellent discharge performance, and they have low self-discharge and large-current resistance capacity. Small size batteries are capable for a wide range of applications. Their designed service life is 3-5 years, and we provide 12-month quality warranty for them. Our batteries can meet with many demanding technical and quality requirements form our customers.

Application

- Emergency lighting

- Security and burglar alarm systems

- Electric toys and power tools

- Telephone and telecommunication equipment

- Computer UPS

- Medical equipments and instruments

General Features

- Sealed and maintenance free operation

- Not restricted from air transport-complies with IATA/ICAO Special Provision A67.

- UL-recognized components

- Safety valve installation for explosion proof

- Excellent deep discharge recovery performance

- Low self-discharge ratio

- Long service life, float or cycle-use applications

| Component | Positive plate | Negative plate | Container | Cover | Safety valve | Terminal | Separator | Electrolyte |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Material | Lead dioxide | Lead | ABS | ABS | Rubber | Copper | AGM glass | Sulfuric acid |

BAT-12V12AH         12V12AH/20HR

General Specifications

| Battery Model | BAT-12V12AH(12V12AH/20 HR) |
| --- | --- |
| Designed Service Life | 5 years |
| Capacity (25℃) | 20HR (0.60A) | 10HR (1.08A) | 5HR (2.04A) | 1HR (7.8A) |
|  | 12.0AH | 10.8AH | 10.2AH | 7.8AH |
| Dimension: mm (inch) | Length | Width | Height | Total Height |
|  | 151 (5.94) | 98.5(3.88) | 98.5(3.88) | 103.5(4.06) |
| Approx. Weight | 3.50Kg (7.72lbs) |
| Internal Resistance | Fully charged at 25℃: 0.03 Ohm |
| Self-discharge | 3% of capacity declined per month at 25℃ |
| Capacity Affected by Temp. (20HR) | 40℃ | 25℃ | 0℃ | -15℃ |
|  | 105% | 100% | 85% | 65% |
| Charge Voltage (25℃) | Cycle use | Stand-by use |
|  | 14.40-15.00V(-30mV/℃) Max. Current: 3.6A | 13.50-13.80V (-20mV/℃) |

Performance Curves and Charts

| Discharge Characteristic (25℃) | Charge Characteristic (25℃) |
| --- | --- |
| Effect of temperature on capacity | Number of cycles Vs. Depth of Discharge |

BAT-12V12AH            12V12AH/20HR

Constant Current Discharge Data

| Constant Current Discharge Data Sheet (Amperes at 25℃) |
| --- |
| End Voltage/cell | Minute (s) | Hour (s) |
|  | 5 | 10 | 15 | 30 | 1 | 3 | 5 | 10 | 20 |
| 1.80 | 40.60 | 28.80 | 22.60 | 12.70 | 7.75 | 3.06 | 2.02 | 1.12 | 0.59 |
| 1.75 | 42.10 | 29.00 | 23.20 | 13.00 | 7.85 | 3.09 | 2.05 | 1.14 | 0.60 |
| 1.70 | 43.50 | 29.90 | 23.70 | 13.30 | 7.94 | 3.12 | 2.07 | 1.16 | 0.61 |
| 1.65 | 45.00 | 30.80 | 24.30 | 13.50 | 8.04 | 3.15 | 2.10 | 1.17 | 0.61 |
| 1.60 | 46.40 | 31.70 | 24.80 | 13.80 | 8.14 | 3.18 | 2.12 | 1.18 | 0.61 |

Constant Power Discharge Data

| Constant Power Discharge Data Sheet (Watts at 25℃) |
| --- |
| End Voltage/cell | Minute (s) | Hour (s) |
|  | 5 | 10 | 15 | 30 | 45 | 1 | 2 | 3 | 5 |
| 1.80 | 77.60 | 54.60 | 43.90 | 25.40 | 19.60 | 15.50 | 8.16 | 6.24 | 4.08 |
| 1.75 | 79.80 | 55.60 | 44.60 | 25.80 | 19.90 | 15.70 | 8.25 | 6.31 | 4.11 |
| 1.70 | 81.90 | 56.60 | 45.30 | 26.20 | 20.10 | 15.80 | 8.33 | 6.37 | 4.14 |
| 1.65 | 84.10 | 57.70 | 46.00 | 26.60 | 20.40 | 16.00 | 8.42 | 6.44 | 4.17 |
| 1.60 | 86.20 | 58.70 | 46.70 | 27.00 | 20.60 | 16.10 | 8.50 | 6.50 | 4.20 |

End Voltage

| Discharge Rate | Discharge Current | End Voltage（V/cell） |
| --- | --- | --- |
| 20h | 0.05C20 A (I20) | 1.75 |
| 10h | 0.09C20 A (I10) | 1.75 |
| 3h | 0.25C20 A (I3) | 1.75 |
| 1h | 0.60C20 A (I1) | 1.60 |

Storage Time VS Charge Time

| Storage Time | Top up Charging Recommendation |
| --- | --- |
| Less than 6 months from production or previous top up charge | Maximum of 16 hours at a constant voltage of 2.40VPC |
| Less than 12 months from production or previous top up charge | Maximum of 20 hours at a constant voltage of 2.40VPC |
| Less than 6 months from production or previous top up charge | Maximum of 8 hours at a constant current of 0.1 C A |
| Less than 12 months from production or previous top up charge | Maximum of 10 hours at a constant current of 0.1 C A |