BAT-12V4.5AH      12V4.5AH/20HR

Standard Terminal Dimensions

Battery Construction

Small Size

Small Size VRLA batteries enjoy excellent discharge performance, and they have low self-discharge and large-current resistance capacity. Small size batteries are capable for a wide range of applications. Their designed service life is 3-5 years, and we provide 12-month quality warranty for them. Our batteries can meet with many demanding technical and quality requirements form our customers.

Application

- Emergency lighting

- Security and burglar alarm systems

- Electric toys and power tools

- Telephone and telecommunication equipment

- Computer UPS

- Medical equipments and instruments

General Features

- Sealed and maintenance free operation

- Not restricted from air transport-complies with IATA/ICAO Special Provision A67.

- UL-recognized components

- Safety valve installation for explosion proof

- Excellent deep discharge recovery performance

- Low self-discharge ratio

- Long service life, float or cycle-use applications

| Component | Positive plate | Negative plate | Container | Cover | Safety valve | Terminal | Separator | Electrolyte |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Material | Lead dioxide | Lead | ABS | ABS | Rubber | Copper | AGM glass | Sulfuric acid |

BAT-12V4.5AH      12V4.5AH/20HR

General Specifications

| Battery Model | BAT-12V4.5AH(12V4.5AH/20 HR) |
| --- | --- |
| Designed Service Life | 5 years |
| Capacity (25℃) | 20HR (0.225A) | 10HR (0.405A) | 5HR (0.765A) | 1HR (2.93A) |
|  | 4.5AH | 4.05AH | 3.83AH | 2.93AH |
| Dimension: mm (inch) | Length | Width | Height | Total Height |
|  | 90 (3.54) | 70(2.76) | 102(4.02) | 106(4.17) |
| Approx. Weight | 1.55 Kg (3.42 lbs) |
| Internal Resistance | Fully charged at 25℃: 0.035 Ohm |
| Self-discharge | 3% of capacity declined per month at 25℃ |
| Capacity Affected by Temp. (20HR) | 40℃ | 25℃ | 0℃ | -15℃ |
|  | 105% | 100% | 85% | 65% |
| Charge Voltage (25℃) | Cycle use | Stand-by use |
|  | 14.40-15.00V(-30mV/℃) Max. Current: 1.35A | 13.50-13.80V (-20mV/℃) |

Performance Curves and Charts

| Discharge Characteristic (25℃) | Charge Characteristic (25℃) |
| --- | --- |
| Effect of temperature on capacity | Number of cycles Vs. Depth of Discharge |

BAT-12V4.5AH        12V4.5AH/20HR

Constant Current Discharge Data

| Constant Current Discharge Data Sheet (Amperes at 25℃) |
| --- |
| End Voltage/cell | Minute (s) | Hour (s) |
|  | 5 | 10 | 15 | 30 | 1 | 3 | 5 | 10 | 20 |
| 1.80 | 13.80 | 11.50 | 8.06 | 4.37 | 2.84 | 1.17 | 0.76 | 0.44 | 0.223 |
| 1.75 | 14.80 | 12.20 | 8.54 | 4.85 | 2.98 | 1.23 | 0.79 | 0.45 | 0.225 |
| 1.70 | 15.70 | 12.90 | 9.01 | 4.85 | 3.12 | 1.28 | 0.81 | 0.46 | 0.227 |
| 1.65 | 16.70 | 13.60 | 9.46 | 5.07 | 3.25 | 1.33 | 0.84 | 0.47 | 0.231 |
| 1.60 | 17.60 | 14.30 | 9.90 | 5.28 | 3.37 | 1.37 | 0.86 | 0.48 | 0.235 |

Constant Power Discharge Data

| Constant Power Discharge Data Sheet (Watts at 25℃) |
| --- |
| End Voltage/cell | Minute (s) | Hour (s) |
|  | 5 | 10 | 15 | 30 | 45 | 1 | 2 | 3 | 5 |
| 1.80 | 25.20 | 18.40 | 14.60 | 8.73 | 6.73 | 5.48 | 3.37 | 2.31 | 1.59 |
| 1.75 | 27.20 | 19.80 | 15.60 | 9.31 | 7.14 | 5.79 | 3.52 | 2.39 | 1.63 |
| 1.70 | 29.20 | 21.20 | 16.6 | 9.89 | 7.55 | 6.09 | 3.67 | 2.46 | 1.67 |
| 1.65 | 31.30 | 22.60 | 17.70 | 10.50 | 7.95 | 6.39 | 3.80 | 2.53 | 1.70 |
| 1.60 | 33.30 | 24.00 | 18.70 | 11.00 | 8.33 | 6.67 | 3.91 | 2.59 | 1.73 |

End Voltage

| Discharge Rate | Discharge Current | End Voltage（V/cell） |
| --- | --- | --- |
| 20h | 0.05C20 A (I20) | 1.75 |
| 10h | 0.09C20 A (I10) | 1.75 |
| 3h | 0.25C20 A (I3) | 1.75 |
| 1h | 0.60C20 A (I1) | 1.60 |

Storage Time VS Charge Time

| Storage Time | Top up Charging Recommendation |
| --- | --- |
| Less than 6 months from production or previous top up charge | Maximum of 16 hours at a constant voltage of 2.40VPC |
| Less than 12 months from production or previous top up charge | Maximum of 20 hours at a constant voltage of 2.40VPC |
| Less than 6 months from production or previous top up charge | Maximum of 8 hours at a constant current of 0.1 C A |
| Less than 12 months from production or previous top up charge | Maximum of 10 hours at a constant current of 0.1 C A |