BAT-12V7.5AH     12V7.5AH/20HR

Standard Terminal Dimensions

Battery Construction

Small-size

Small Size VRLA batteries enjoy excellent discharge performance, and they have low self-discharge and large-current resistance capacity. Small size batteries are capable for a wide range of applications. Their designed service life is 3-5 years, and we provide 12-month quality warranty for them. Our batteries can meet with many demanding technical and quality requirements form our customers.

Application

- Emergency lighting

- Security and burglar alarm systems

- Electric toys and power tools

- Telephone and telecommunication equipment

- Computer UPS

- Medical equipments and instruments

General Features

- Sealed and maintenance free operation

- Not restricted from air transport-complies with IATA/ICAO Special Provision A67.

- UL-recognized components

- Safety valve installation for explosion proof

- Excellent deep discharge recovery performance

- Low self-discharge ratio

- Long service life, float or cycle-use applications

| Component | Positive plate | Negative plate | Container | Cover | Safety valve | Terminal | Separator | Electrolyte |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Material | Lead dioxide | Lead | ABS | ABS | Rubber | Copper | AGM glass | Sulfuric acid |

BAT-12V7.5AH     12V7.5AH/20HR

General Specifications

| Battery Model | BAT-12V7.5AH(12V7.5AH/20 HR) |
| --- | --- |
| Designed Service Life | 5 years |
| Capacity (25℃) | 20HR (0.375A) | 10HR (0.65A) | 5HR (1.28A) | 1HR (4.50A) |
|  | 7.6AH | 6.65AH | 6.40AH | 4.50AH |
| Dimension: mm (inch) | Length | Width | Height | Total Height |
|  | 151 (5.94) | 65(2.56) | 94(3.70) | 99(3.90) |
| Approx. Weight | 2.21Kg (4.9 lbs) |
| Internal Resistance | Fully charged at 25℃: 0.03 Ohm |
| Self-discharge | 3% of capacity declined per month at 25℃ |
| Capacity Affected by Temp. (20HR) | 40℃ | 25℃ | 0℃ | -15℃ |
|  | 105% | 100% | 85% | 65% |
| Charge Voltage (25℃) | Cycle use | Stand-by use |
|  | 14.40-15.00V(-30mV/℃) Max. Current: 2.25 A | 13.50-13.80V (-20mV/℃) |

Performance Curves and Charts

| Discharge Characteristic (25℃) | Charge Characteristic (25℃) |
| --- | --- |
| Effect of temperature on capacity | Number of cycles Vs. Depth of Discharge |

BAT-12V7.5AH     12V7.5AH/20HR

Constant Current Discharge Data

| Constant Current Discharge Data Sheet (Amperes at 25℃) |
| --- |
| End Voltage/cell | Minute (s) | Hour (s) |
|  | 5 | 10 | 15 | 30 | 1 | 3 | 5 | 10 | 20 |
| 1.80 | 23.10 | 16.80 | 13.40 | 7.63 | 4.69 | 1.79 | 1.24 | 0.72 | 0.385 |
| 1.75 | 25.80 | 17.30 | 14.30 | 8.12 | 4.86 | 1.85 | 1.25 | 0.72 | 0.385 |
| 1.70 | 27.80 | 197.90 | 14.60 | 8.39 | 4.98 | 1.91 | 1.27 | 0.73 | 0.385 |
| 1.65 | 28.80 | 19.30 | 14.90 | 8.56 | 5.07 | 1.95 | 1.29 | 0.73 | 0.390 |
| 1.60 | 30.60 | 18.90 | 15.30 | 8.77 | 5.12 | 1.98 | 1.30 | 0.73 | 0.390 |

Constant Power Discharge Data

| Constant Power Discharge Data Sheet (Watts at 25℃) |
| --- |
| End Voltage/cell | Minute (s) | Hour (s) |
|  | 5 | 10 | 15 | 30 | 45 | 1 | 2 | 3 | 5 |
| 1.80 | 44.70 | 33.00 | 26.70 | 15.30 | 12.00 | 9.32 | 5.26 | 3.58 | 2.33 |
| 1.75 | 50.70 | 34.20 | 28.30 | 16.10 | 12.40 | 9.66 | 5.34 | 3.72 | 2.39 |
| 1.70 | 54.50 | 35.40 | 29.10 | 16.70 | 12.80 | 9.94 | 5.40 | 3.85 | 2.42 |
| 1.65 | 56.20 | 36.30 | 29.90 | 17.00 | 13.00 | 10.10 | 5.45 | 3.95 | 2.45 |
| 1.60 | 58.10 | 37.10 | 30.40 | 17.40 | 13.10 | 10.20 | 5.50 | 3.96 | 2.48 |

End Voltage

| Discharge Rate | Discharge Current | End Voltage（V/cell） |
| --- | --- | --- |
| 20h | 0.05C20 A (I20) | 1.75 |
| 10h | 0.09C20 A (I10) | 1.75 |
| 3h | 0.25C20 A (I3) | 1.75 |
| 1h | 0.60C20 A (I1) | 1.60 |

Storage Time VS Charge Time

| Storage Time | Top up Charging Recommendation |
| --- | --- |
| Less than 6 months from production or previous top up charge | Maximum of 16 hours at a constant voltage of 2.40VPC |
| Less than 12 months from production or previous top up charge | Maximum of 20 hours at a constant voltage of 2.40VPC |
| Less than 6 months from production or previous top up charge | Maximum of 8 hours at a constant current of 0.1 C A |
| Less than 12 months from production or previous top up charge | Maximum of 10 hours at a constant current of 0.1 C A |